**FILT’RAY 4-month shower head**

Non-sterile

Shower spray

Reference: **AT030725**

Specification description

AQUATOOLS anti-Legionella and all-germ shower filter.

Device made from MBS.

Membrane type: tubular microfiltration.

Membrane made from polyethylene.

Pore cut-off threshold: 0.1μm nominal and 0.2μm absolute sterilising grade.

Filtration flow rate: 9 lpm at 3 bar and 6 lpm at 1 bar

(filter only, excludes any flow rate restriction in the shower).

Maximum upstream pressure at the point-of-use: 5 bar.

Maximum lifespan: 4 months from installation.

Withstands thermal shocks: 70°C for 30 minutes.

Withstands chemical shocks: active chlorine levels up to 100 ppm for 4 hours (cumulative total).

Non-sterile filter.

CE marked Class I medical device.

Packaged in boxes of 10.