FILT&SWAP inline filter

Active charcoal

Reference: AT50672

Specification description

FILT&SWAP active charcoal inline filter.

Active charcoal: reduces taste, smell and chlorine in water.

Filter cartridge can be replaced without changing the filter body.

Capacity: 18,000L.

Maximum lifespan: 6 months.

Filtration flow rate: 9 lpm (with integrated flow restrictor), 14 lpm (without flow restrictor) at 3 bar.

Materials: Body and filtration cartridge made of polypropylene. Filter cartridge plastic components made of ABS.

Temperature: 4 - 38°C.

Operating pressure: 0.5 - 10 bar.

Connection type: Tube or G3/8".

Compatible with and resistant to chemical shocks (active chlorine levels up to 100 ppm for 1 hour (cumulative total) and thermal shocks (70°C for 30 minutes).